## Instructions
PID CONTROLLER TUNNING PARAMETERS SIMULATOR
This Excelsheet simulates PID controller tunning parameters response
Note: This excel file simulates an "academic" version of the PID controller. PID controllers used in industry are different from this version. This simulator consists of controller gains, Process variable gains and used PID calculation formulae are theoretical only. The practical PID controller will differ from this simulator and this simulation will only used to understand the PID controller tunning parameters effect on the manipulated variable with respect to error value.
Here we can simulate a process variable or create a disturbance and observe the PID controller response with different set of PID controller gains.
This simulator designed for a Five minutes time span only, so the process variables values and PID controller gains value ranges are limited.
Steps to Follow
Here we are giving an fixed step change input to the setpoint of a PID controller.
In Parameters sheet we can get the Process parameters & PID Controllers gains or you can use your own.
Enter the Process Parameters values (K,T & L) for simulating a Process variable (PV).
Enter the PID Controller Parameters values (C, I & D) for simulating PID Controllers action.
Understand the Process variable & PID controllers response from the graph.
Repeat above procedure for different controllers and observe the response
INDEX
Sheet 1 contains basic instructions for using this excel PID controller simulator.
Sheet 2 contains the PID Controller Simulator.
Sheet 3 contains various types of parameters set for different PID controllers.
Sheet 4 contains baisc theory of a PID controller philosphy.
Sheet 5 contains baiscs of PID simulator functions.
Sheet 6 contains PID controller calculations.
Happy Learning
S Bharadwaj Reddy

## PID TUNNING
PID CONTROLLER TUNNING PARAMETERS SIMULATOR
ENTER BELOW PARAMETERS FOR SIMULATION
The above block diagram shows the basic closed loop PID controller. The theoritical formulas for PID controller & Process are shown in picture.
(All times in seconds)
PROCESS VALUE SIMULATION
Process Parameters
|  | Gain (K) | 1
|  | Time Constant (T) | 5
|  | Delay (L) | 5
PID CONTROLLER SIMULATION
PID Controller Parameters
|  | Proportional Gain (C) | 0.1
|  | Integral (I) | 5
|  | Derivative (D) | 1
COLOUR INDEX
Process Variable Parameters
PID Controller Parameters
Note:
1. Enter different values and simulate the process variable and observe the PID controller response for the respective tunning parameters.
2. As the above time scale was created for a period of 5 minute so range of parameters to be entered are limited.
PID CONTROLLER
C + 1/Is + Ds
PROCESS
K/(1+Ts) * e^(-Ls)
SETPOINT
SP
+
-
OUTPUT
MV
PROCESS VALUE
PV
PV
InstrumentationTools.com

## Parameters
SIMULATION PARAMETERS
S.No. | Type of Controller | Process Parameters (PV) |  |  | PID Controller Parameters |  |  | Remarks
|  | Gain (K) | Time Constant (T) | Delay (L) | Proportional Gain (C) | Integral (I) | Derivative (D)
1 | PID Controller | 1 | 5 | 5 | 0.1 | 5 | 1 | PID gains
2 | PI Controller | 1 | 5 | 5 | 0.5 | 5 | 0 | D = 0
3 | P Controller | 1 | 5 | 5 | 1.5 | 0 | 0 | I = 0, D = 0
4 | I Controller | 1 | 5 | 5 | 0 | 5 | 0 | P = 0, D = 0
5 | D Controller | 1 | 5 | 5 | 0 | 0 | 5 | P = 0, I = 0
Enter the above shown parameters in PID tunning Sheet (Sheet No.2)
The above table shows different parameters for various types of controllers.You can use your own parameter values & Controller gains for simulating Process Variable and PID controller response. Make sure the data entered values genertate a graph within a period of 5minutes timespan so that we can understand the controllers response easily. This excel simulator is limited for a 5 minutes timespan only.
NOTE:
Process Parameters: These Parameters are required to Simulate a Process variable
PID Controller Parameters: These Parameters are required to simulate the PID controllers action.

## PID Controller Theory
PID CONTROLLER & TUNNING THEORY
Anatomy of a Feedback Control System
Here is the classic block diagram of a process under PID Control.
What’s going on this diagram?
The Setpoint (SP) is the value that we want the process to be.
For example, the temperature control system in our house may have a SP of 22°C. This means that
“We want the heating and cooling process in our house to achieve a steady temperature of as close to 22°C as possible”
The PID controller looks at the setpoint and compares it with the actual value of the Process Variable (PV). Back in our house, the box of electronics that is the PID controller in our Heating and cooling system looks at the value of the temperature sensor in the room and sees how close it is to 22°C.
If the SP and the PV are the same – then the controller is a very happy little box. It doesn’t have to do anything; it will set its output remain same value.
However, if there is a disparity between the SP and the PV we have an error and corrective action is needed. In our house this will either be cooling or heating depending on whether the PV is higher or lower than the SP respectively.
Let’s imagine the temperature PV in our house is higher than the SP. It is too hot. The air-con is switched on and the temperature drops.
The sensor picks up the lower temperature, feeds that back to the controller, the controller sees that the “temperature error” is not as great because the PV (temperature) has dropped and the air con is turned down a little.
This process is repeated until the house has cooled down to 22°C and there is no error.
Then a disturbance hits the system and the controller has to kick in again.
In our house the disturbance may be the sun beating down on the roof, raising the temperature of the air inside.
So that’s a really, really basic overview of a simple feedback control system. Sounds dead simple eh?
Understanding the controller
Unfortunately, in the real world we need a controller that is a bit more complicated than the one described above, if we want top performance form our loops. To understand why, we will be doing some “thought experiments” where we are the controller.
When we have gone through these thought experiments we will appreciate why a PID algorithm is needed and why/how it works to control the process.
We will be using the analogy of changing lanes on a freeway on a windy day. We are the driver, and therefore the controller of the process of changing the car’s position.
Here’s the Block Diagram we used before, with the labels changed to represent the car-on-windy-freeway control loop.
Notice how important closing the feedback loop is. If we removed the feedback loop we would be in “open loop control”, and would have to control the car’s position with our eyes closed!
Thankfully we are under “Closed loop control” -using our eyes for position feedback.
As we saw in the house-temperature example the controller takes the both the PV and SP signals, which it then puts through a black box to calculate a controller output. That controller output is sent to an actuator which moves to actually control the process.
We are interested here in what the controller actually does, which is that it applies 1, 2 or 3 calculations to the SP and Measured PV signals. These calculations, called the “Modes of Control” include:
Proportional (P)
Integral (I)
Derivative (D)
Under The Hood of The PID Controller
Here’s a simplified block diagram of what the PID controller does:
It is really very simple in operation. The PV is subtracted from the SP to create the Error. The error is simply multiplied by one, two or all of the calculated P, I and D actions (depending which ones are turned on). Then the resulting “error x control actions” are added together and sent to the controller output.
These 3 modes are used in different combinations:
P – Sometimes used
PI - Most often used
PID – Sometimes used
PD – rarely used but can be useful for controlling servomotors.
Derivatives
Go into the control room of a process plant and ask the operator:
“What’s the derivative of reactor 4’s pressure?”
And the response will typically be:
“Bugger off smart arse!”
However go in and ask:
“What’s the rate of change of reactor 4’s pressure?”
And the operator will examine the pressure trend and say something like:
“About 5 PSI every 10 minutes”
He’s just performed calculus on the pressure trend! (Don’t tell him though or he’ll want a pay raise)
So derivative is just a mathematical term meaning rate-of-change. That’s all there is to it.
Integratives
Is it any wonder that so many people run scared from the concept of integrals and integration, when this is a typical definition?
The integral of a signal is the sum of all the instantaneous values that the signal has been, from whenever you started counting until you stop counting.
So if you are to plot your signal on a trend and your signal is sampled every second, and let’s say you are measuring temperature. If you were to superimpose the integral of the signal over the first 5 seconds – it would look like this:
The green line is your temperature, the red circles are where your control system has sampled the temperature and the blue area is the integral of the temperature signal. It is the sum of the 5 temperature values over the time period that you are interested in. In numerical terms it is the sum of the areas of each of the blue rectangles:
(13 x 1)+(14x1)+(13x1)+(12x1)+(11x1) = 63 °C s
The curious units (degrees Celsius x seconds) are because we have to multiply a temperature by a time – but the units aren’t important.
As you can probably remember from school –the integral turns out to be the area under the curve. When we have real world systems, we actually get an approximation to the area under the curve, which as you can see from the diagram gets better, the faster we sample.
Proportional control
Here’s a diagram of the controller when we have enabled only P control:
In Proportional Only mode, the controller simply multiplies the Error by the Proportional Gain (Kp) to get the controller output.
The Proportional Gain is the setting that we tune to get our desired performance from a “P only” controller.
A match made in heaven: The P + I Controller
If we put Proportional and Integral Action together, we get the humble PI controller. The Diagram below shows how the algorithm in a PI controller is calculated.
The tricky thing about Integral Action is that it will really screw up your process unless you know exactly how much Integral action to apply.
Adjusting the Integral Action
The way to adjust how much Integral Action you have is by adjusting a term called “minutes per repeat”. Not a very intuitive name is it?
So where does this strange name come from? It is a measure of how long it will take for the Integral Action to match the Proportional Action.
In other words, if the output of the proportional box on the diagram above is 20%, the repeat time is the time it will take for the output of the Integral box to get to 20% too.
And the important point to note is that the “bigger” integral action, the quicker it will get this 20% value. That is, it will take fewer minutes to get there, so the “minutes per repeat” value will be smaller.
In other words the smaller the “minutes per repeat” is the bigger the integral action.
To make things a bit more intuitive, a lot of controllers use an alternative unit of “repeats per minute” which is obviously the inverse of “minutes per repeat”.
The nice thing about “repeats per minute” is that the bigger it is - the bigger the resulting Integral action is.
Derivative Action – predicting the future
OK, so the combination of P and I action seems to cover all the bases and do a pretty good job of controlling our system. That is the reason that PI controllers are the most prevalent. They do the job well enough and keep things simple. Great.
But engineers being engineers are always looking to tweak performance.
They do this in a PID loop by adding the final ingredient: Derivative Action.
So adding derivative action can allow you to have bigger P and I gains and still keep the loop stable, giving you a faster response and better loop performance.
If you think about it, Derivative action improves the controller action because it predicts what is yet to happen by projecting the current rate of change into the future. This means that it is not using the current measured value, but a future measured value.
The units used for derivative action describe how far into the future you want to look. i.e. If derivative action is 20 seconds, the derivative term will project the current rate of change 20 seconds into the future.
The big problem with D control is that if you have noise on your signal (which looks like a bunch of spikes with steep sides) this confuses the hell out of the algorithm. It looks at the slope of the noise-spike and thinks:
“Holy crap! This process is changing quickly, lets pile on the D Action!!!”
And your control output jumps all over the place, messing up your control.
Of course you can try and filter the noise out, but my advice is that, unless PI control is really slow, don’t worry about switching D on.
Finally understand the knowledge of P, I & D Controllers Philosophy and apply the same to your process requirement and tune the controllers with maximum bumpless control.
Happy Learning
S Bharadwaj Reddy

## Simulator Theory
Modelling the Process
To use the simulator, we need a model of the process. Here we are simulating the process variable response with a standard equation.
Most chemical processes fall into one of 2 categories - first order process with dead time (FOPDT) and integrating processes with dead time.
An FOPDT process is characterised by 3 parameters:
1. Process Gain - the ratio of the change in process variable to the ratio of the change in manipulated variable
2. Time constant - which measures the speed of response
3. Dead time - time between moving the manipulated variable and start of the process response
One of the most common ways of obtaining these parameters is by doing a step test. To do this, wait for the process to be steady and then step the Manipulated Variable (MV). The process variable (PV) will move as shown below.
Calculate the parameters as follows:
Dimensionless Gain = (Change in PV/PV range)/(Change in MV/MV Range)
Time constant = Time taken for the PV to change by 63.2% of the final change
Dead time = Time for the PV to start moving after the change in the MV
For the step response shown in the figure above, Dimensionless Gain = (10/200)/(5/100), where PV range = 200 units and MV range = 100 units
Time constant = 30 sec
Dead time = 60 sec
Key in these parameters into the simulator and study the effects of changing the tuning parameters on the response of the system.
The Response
The response of a delay free first order system is described by:
Change in PV = Process gain x (1 - exp(-Time/Time Constant))x Change in MV
Since the final change in PV = Process gain x Change in MV, this equation can be written as
Change in PV = Final Change in PV x (1 - exp(-Time/Time Constant))
At time = time constant,
Change in PV = (1 - exp(-1)) x Final Change in PV = 0.632 x Final Change in PV or 63.2% of the final change in the PV
Typical process values
In a chemical process, flow loops are often the fastest, with gains ranging from 1 to 10, time constant ranging from a few seconds to a couple of minutes and a few seconds of dead time.
Temperature loops are usually much slower with both dead time and response time in the range of a few minutes.
Often, the slowest loops are online analyzer loops, these often have a dead time half an hour or more.
How to use simulator
Here the process is simulated by the process gain, time constant and dead. The PID controller has 3 parameters: gain, integral and derivative. Key in these values into the appropriate cells. If the integral time is keyed in as 0, the integral term is ignored.
The response to a step change in the set point is displayed in the chart.
The screenshot below shows an example of the inputs and the output chart.
The calculations required for the simulation are done on Sheet2. Defined Formulae are used in the computation.
The first order process is calculated using a difference equation, given by:
Process Value = b x (Output at time offset by delay time) - a x Last PV; where
a = - exp ( -1 / Process Time Constant) and
b = Process Gain x (1 + a)
The error is calculated by taking the difference between the PV and SP values. The error values are accumulated in column F for the integral term calculation and the derivative term is calculated by taking the difference between the current error and the last error. The PID calculation determines the next output value. The PID calculation is:
Next output = Controller Gain x error + Accumulated error / Integral time + Derivative x (Current error - Previous error)
Note that this excel file simulates an "academic" version of the PID controller. PID controllers used in industry are different from this version. This simulator controller gains, Process gains and used calculation formulae are theoretical only. The practical PID controller will differ from this simulator and this simulation will only used to understand the PID controller tunning parameters effect on the manipulated variable with respect to error value.
Setting the PID parameters (controller gain, integral and derivative times) to achieve a desired process response is known as loop tuning. A well tuned loop takes the process value to the set point within the desired time frame, removes disturbances and can tolerate some variations or uncertainities in the process (i.e., it is robust).
There are 2 aspects of loop tuning - performance and robustness. Performance means that when the set point is changed, the controller should bring the process value to the new set point within the desired time. Robustness means that the controller should maintain control even if there are changes to the process. Performance is often given importance, while robustness is ignored.
Often measures of disturbances or uncertainities or even desired settling times are difficult to get and the control engineer has to have a feel for the process to tune the loop correctly.
For this reason, loop tuning is considered both an art and a science.
While the art portion of tuning is developed with experience.
Happy Learning
S Bharadwaj Reddy

## Calculation
t | SP | OP | PV | Error | AccumErr
-10 | 0 | 0 | 0 | 0 | 0 | DONOT TOUCH THIS SHEET FOR INTERNAL CALCULATION ONLY
-9 | 0 | 0 | 0 | 0 | 0
-8 | 0 | 0 | 0 | 0 | 0
-7 | 0 | 0 | 0 | 0 | 0
-6 | 0 | 0 | 0 | 0 | 0
-5 | 0 | 0 | 0 | 0 | 0
-4 | 0 | 0 | 0 | 0 | 0
-3 | 0 | 0 | 0 | 0 | 0
-2 | 0 | 0 | 0 | 0 | 0
-1 | 0 | 0 | 0 | 0 | 0
0 | 1 | 1.3 | 0 | 1 | 1
1 | 1 | 0.5 | 0 | 1 | 2
2 | 1 | 0.7 | 0 | 1 | 3
3 | 1 | 0.9 | 0 | 1 | 4
4 | 1 | 1.1 | 0 | 1 | 5
5 | 1 | 1.3 | 0 | 1 | 6
6 | 1 | 1.1937 | 0.23565 | 0.76435 | 6.7643
7 | 1 | 1.5199 | 0.28357 | 0.71643 | 7.4808
8 | 1 | 1.613 | 0.35905 | 0.64095 | 8.1217
9 | 1 | 1.6892 | 0.45711 | 0.54289 | 8.6646
10 | 1 | 1.7443 | 0.57365 | 0.42635 | 9.091
11 | 1 | 1.7749 | 0.70531 | 0.29469 | 9.3857
12 | 1 | 1.8505 | 0.79383 | 0.20617 | 9.5918
13 | 1 | 1.8091 | 0.92544 | 0.074556 | 9.6664
14 | 1 | 1.7936 | 1.0501 | -0.050068 | 9.6163
15 | 1 | 1.7576 | 1.1659 | -0.16592 | 9.4504
16 | 1 | 1.704 | 1.2708 | -0.27076 | 9.1796
17 | 1 | 1.6359 | 1.3621 | -0.36215 | 8.8175
18 | 1 | 1.5398 | 1.4507 | -0.45066 | 8.3668
19 | 1 | 1.4537 | 1.5156 | -0.51564 | 7.8512
20 | 1 | 1.35 | 1.566 | -0.56603 | 7.2851
21 | 1 | 1.2421 | 1.6008 | -0.60077 | 6.6844
22 | 1 | 1.1323 | 1.6195 | -0.61948 | 6.0649
23 | 1 | 1.0233 | 1.6225 | -0.62245 | 5.4424
24 | 1 | 0.92123 | 1.6075 | -0.60747 | 4.835
25 | 1 | 0.82099 | 1.5796 | -0.57959 | 4.2554
26 | 1 | 0.73129 | 1.538 | -0.53798 | 3.7174
27 | 1 | 0.65182 | 1.4843 | -0.48434 | 3.2331
28 | 1 | 0.58426 | 1.4205 | -0.42053 | 2.8125
29 | 1 | 0.52996 | 1.3485 | -0.34852 | 2.464
30 | 1 | 0.48894 | 1.2711 | -0.27107 | 2.1929
31 | 1 | 0.46333 | 1.1895 | -0.18948 | 2.0035
32 | 1 | 0.45182 | 1.1064 | -0.10643 | 1.897
33 | 1 | 0.45461 | 1.024 | -0.02402 | 1.873
34 | 1 | 0.47103 | 0.94431 | 0.055695 | 1.9287
35 | 1 | 0.50009 | 0.8692 | 0.1308 | 2.0595
36 | 1 | 0.54075 | 0.80027 | 0.19973 | 2.2592
37 | 1 | 0.59117 | 0.73919 | 0.26081 | 2.5201
38 | 1 | 0.64997 | 0.6871 | 0.3129 | 2.833
39 | 1 | 0.71525 | 0.64496 | 0.35504 | 3.188
40 | 1 | 0.7851 | 0.61343 | 0.38657 | 3.5746
41 | 1 | 0.85759 | 0.59288 | 0.40712 | 3.9817
42 | 1 | 0.93076 | 0.58343 | 0.41657 | 4.3983
43 | 1 | 1.0028 | 0.58484 | 0.41516 | 4.8134
44 | 1 | 1.0719 | 0.59664 | 0.40336 | 5.2168
45 | 1 | 1.1364 | 0.61814 | 0.38186 | 5.5986
46 | 1 | 1.1949 | 0.64841 | 0.35159 | 5.9502
47 | 1 | 1.2462 | 0.68633 | 0.31367 | 6.2639
48 | 1 | 1.2893 | 0.73063 | 0.26937 | 6.5333
49 | 1 | 1.3233 | 0.77997 | 0.22003 | 6.7533
50 | 1 | 1.3479 | 0.83288 | 0.16712 | 6.9204
51 | 1 | 1.3627 | 0.8879 | 0.1121 | 7.0325
52 | 1 | 1.3678 | 0.94356 | 0.056439 | 7.089
53 | 1 | 1.3634 | 0.99843 | 0.001575 | 7.0905
54 | 1 | 1.35 | 1.0511 | -0.051148 | 7.0394
55 | 1 | 1.3284 | 1.1005 | -0.10049 | 6.9389
56 | 1 | 1.2993 | 1.1453 | -0.14533 | 6.7936
57 | 1 | 1.2639 | 1.1847 | -0.18473 | 6.6088
58 | 1 | 1.2232 | 1.2179 | -0.21791 | 6.3909
59 | 1 | 1.1785 | 1.2443 | -0.24428 | 6.1466
60 | 1 | 1.1311 | 1.2635 | -0.26345 | 5.8832
61 | 1 | 1.0823 | 1.2752 | -0.27523 | 5.608
62 | 1 | 1.0333 | 1.2796 | -0.2796 | 5.3284
63 | 1 | 0.98549 | 1.2767 | -0.27675 | 5.0516
64 | 1 | 0.93991 | 1.267 | -0.26704 | 4.7846
65 | 1 | 0.89766 | 1.251 | -0.251 | 4.5336
66 | 1 | 0.85966 | 1.2293 | -0.22927 | 4.3043
67 | 1 | 0.82671 | 1.2026 | -0.20263 | 4.1017
68 | 1 | 0.79944 | 1.1719 | -0.17194 | 3.9297
69 | 1 | 0.7783 | 1.1381 | -0.13814 | 3.7916
70 | 1 | 0.76359 | 1.1022 | -0.10221 | 3.6894
71 | 1 | 0.75541 | 1.0651 | -0.065131 | 3.6242
72 | 1 | 0.75373 | 1.0279 | -0.027886 | 3.5964
73 | 1 | 0.75831 | 0.99142 | 0.0085804 | 3.6049
74 | 1 | 0.7688 | 0.95662 | 0.043381 | 3.6483
75 | 1 | 0.7847 | 0.9243 | 0.075705 | 3.724
76 | 1 | 0.80539 | 0.89516 | 0.10484 | 3.8289
77 | 1 | 0.83015 | 0.86983 | 0.13017 | 3.959
78 | 1 | 0.85822 | 0.84879 | 0.15121 | 4.1102
79 | 1 | 0.88873 | 0.83239 | 0.16761 | 4.2779
80 | 1 | 0.92084 | 0.82086 | 0.17914 | 4.457
81 | 1 | 0.95366 | 0.81431 | 0.18569 | 4.6427
82 | 1 | 0.98635 | 0.81269 | 0.18731 | 4.83
83 | 1 | 1.0181 | 0.81585 | 0.18415 | 5.0141
84 | 1 | 1.0481 | 0.82353 | 0.17647 | 5.1906
85 | 1 | 1.0757 | 0.83535 | 0.16465 | 5.3553
86 | 1 | 1.1003 | 0.85085 | 0.14915 | 5.5044
87 | 1 | 1.1214 | 0.86949 | 0.13051 | 5.6349
88 | 1 | 1.1386 | 0.89067 | 0.10933 | 5.7443
89 | 1 | 1.1516 | 0.91376 | 0.086236 | 5.8305
90 | 1 | 1.1603 | 0.93811 | 0.061886 | 5.8924
91 | 1 | 1.1646 | 0.96305 | 0.036946 | 5.9293
92 | 1 | 1.1646 | 0.98793 | 0.012068 | 5.9414
93 | 1 | 1.1604 | 1.0121 | -0.012126 | 5.9293
94 | 1 | 1.1524 | 1.0351 | -0.035052 | 5.8942
95 | 1 | 1.1409 | 1.0562 | -0.056184 | 5.838
96 | 1 | 1.1262 | 1.0751 | -0.07506 | 5.763
97 | 1 | 1.109 | 1.0913 | -0.091294 | 5.6717
98 | 1 | 1.0897 | 1.1046 | -0.10458 | 5.5671
99 | 1 | 1.0689 | 1.1147 | -0.11471 | 5.4524
100 | 1 | 1.0472 | 1.1215 | -0.12154 | 5.3308
101 | 1 | 1.0252 | 1.125 | -0.12505 | 5.2058
102 | 1 | 1.0034 | 1.1253 | -0.12526 | 5.0805
103 | 1 | 0.98237 | 1.1223 | -0.1223 | 4.9582
104 | 1 | 0.96265 | 1.1164 | -0.11639 | 4.8418
105 | 1 | 0.94465 | 1.1078 | -0.10778 | 4.7341
106 | 1 | 0.92876 | 1.0968 | -0.096793 | 4.6373
107 | 1 | 0.9153 | 1.0838 | -0.083807 | 4.5535
108 | 1 | 0.90451 | 1.0692 | -0.069226 | 4.4842
109 | 1 | 0.89655 | 1.0535 | -0.053482 | 4.4308
110 | 1 | 0.89151 | 1.037 | -0.037016 | 4.3937
111 | 1 | 0.88941 | 1.0203 | -0.020273 | 4.3735
112 | 1 | 0.89018 | 1.0037 | -0.0036842 | 4.3698
113 | 1 | 0.89368 | 0.98766 | 0.012337 | 4.3821
114 | 1 | 0.89972 | 0.97259 | 0.027411 | 4.4095
115 | 1 | 0.90805 | 0.95881 | 0.041195 | 4.4507
116 | 1 | 0.91836 | 0.94661 | 0.053393 | 4.5041
117 | 1 | 0.93032 | 0.93624 | 0.063761 | 4.5679
118 | 1 | 0.94356 | 0.92789 | 0.07211 | 4.64
119 | 1 | 0.95769 | 0.92169 | 0.078312 | 4.7183
120 | 1 | 0.97233 | 0.91771 | 0.082293 | 4.8006
121 | 1 | 0.98708 | 0.91596 | 0.084044 | 4.8846
122 | 1 | 1.0016 | 0.91639 | 0.083608 | 4.9683
123 | 1 | 1.0155 | 0.91892 | 0.081083 | 5.0493
124 | 1 | 1.0284 | 0.92338 | 0.076616 | 5.126
125 | 1 | 1.0401 | 0.9296 | 0.070397 | 5.1963
126 | 1 | 1.0503 | 0.93735 | 0.062652 | 5.259
127 | 1 | 1.0589 | 0.94636 | 0.053636 | 5.3126
128 | 1 | 1.0656 | 0.95637 | 0.043628 | 5.3563
129 | 1 | 1.0704 | 0.96708 | 0.032919 | 5.3892
130 | 1 | 1.0733 | 0.97819 | 0.021806 | 5.411
131 | 1 | 1.0742 | 0.98941 | 0.010587 | 5.4216
132 | 1 | 1.0731 | 1.0005 | -0.00045386 | 5.4211
133 | 1 | 1.0703 | 1.011 | -0.011044 | 5.4101
134 | 1 | 1.0658 | 1.0209 | -0.020935 | 5.3891
135 | 1 | 1.0599 | 1.0299 | -0.029905 | 5.3592
136 | 1 | 1.0527 | 1.0378 | -0.037765 | 5.3215
137 | 1 | 1.0444 | 1.0444 | -0.044361 | 5.2771
138 | 1 | 1.0353 | 1.0496 | -0.049577 | 5.2275
139 | 1 | 1.0257 | 1.0533 | -0.053337 | 5.1742
140 | 1 | 1.0159 | 1.0556 | -0.055605 | 5.1186
141 | 1 | 1.006 | 1.0564 | -0.056381 | 5.0622
142 | 1 | 0.99641 | 1.0557 | -0.055706 | 5.0065
143 | 1 | 0.98726 | 1.0537 | -0.053655 | 4.9529
144 | 1 | 0.97879 | 1.0503 | -0.050334 | 4.9025
145 | 1 | 0.9712 | 1.0459 | -0.045877 | 4.8566
146 | 1 | 0.96463 | 1.0404 | -0.040441 | 4.8162
147 | 1 | 0.95922 | 1.0342 | -0.034203 | 4.782
148 | 1 | 0.95505 | 1.0274 | -0.027352 | 4.7546
149 | 1 | 0.95217 | 1.0201 | -0.020083 | 4.7346
150 | 1 | 0.95062 | 1.0126 | -0.012598 | 4.722
151 | 1 | 0.95037 | 1.0051 | -0.0050938 | 4.7169
152 | 1 | 0.95138 | 0.99776 | 0.0022408 | 4.7191
153 | 1 | 0.95358 | 0.99077 | 0.0092273 | 4.7283
154 | 1 | 0.95685 | 0.9843 | 0.015704 | 4.744
155 | 1 | 0.96109 | 0.97847 | 0.021527 | 4.7656
156 | 1 | 0.96614 | 0.97342 | 0.026576 | 4.7921
157 | 1 | 0.97183 | 0.96924 | 0.030755 | 4.8229
158 | 1 | 0.97802 | 0.96601 | 0.033993 | 4.8569
159 | 1 | 0.98451 | 0.96375 | 0.036247 | 4.8931
160 | 1 | 0.99113 | 0.9625 | 0.037497 | 4.9306
161 | 1 | 0.99771 | 0.96225 | 0.037753 | 4.9684
162 | 1 | 1.0041 | 0.96295 | 0.037048 | 5.0054
163 | 1 | 1.0101 | 0.96456 | 0.035438 | 5.0409
164 | 1 | 1.0156 | 0.967 | 0.032999 | 5.0739
165 | 1 | 1.0205 | 0.97017 | 0.029826 | 5.1037
166 | 1 | 1.0248 | 0.97397 | 0.026028 | 5.1297
167 | 1 | 1.0282 | 0.97827 | 0.021725 | 5.1515
168 | 1 | 1.0307 | 0.98295 | 0.017046 | 5.1685
169 | 1 | 1.0324 | 0.98788 | 0.012124 | 5.1806
170 | 1 | 1.0332 | 0.99291 | 0.0070917 | 5.1877
171 | 1 | 1.0332 | 0.99792 | 0.0020812 | 5.1898
172 | 1 | 1.0323 | 1.0028 | -0.0027826 | 5.187
173 | 1 | 1.0306 | 1.0074 | -0.0073828 | 5.1796
174 | 1 | 1.0282 | 1.0116 | -0.011614 | 5.168
175 | 1 | 1.0252 | 1.0154 | -0.015385 | 5.1526
176 | 1 | 1.0217 | 1.0186 | -0.018618 | 5.134
177 | 1 | 1.0178 | 1.0213 | -0.021253 | 5.1128
178 | 1 | 1.0136 | 1.0232 | -0.023249 | 5.0895
179 | 1 | 1.0092 | 1.0246 | -0.024579 | 5.0649
180 | 1 | 1.0048 | 1.0252 | -0.025237 | 5.0397
181 | 1 | 1.0004 | 1.0252 | -0.025234 | 5.0145
182 | 1 | 0.99615 | 1.0246 | -0.024595 | 4.9899
183 | 1 | 0.9922 | 1.0234 | -0.023361 | 4.9665
184 | 1 | 0.9886 | 1.0216 | -0.021589 | 4.9449
185 | 1 | 0.98543 | 1.0193 | -0.019343 | 4.9256
186 | 1 | 0.98275 | 1.0167 | -0.016699 | 4.9089
187 | 1 | 0.98061 | 1.0137 | -0.01374 | 4.8951
188 | 1 | 0.97905 | 1.0106 | -0.010552 | 4.8846
189 | 1 | 0.97808 | 1.0072 | -0.0072248 | 4.8774
190 | 1 | 0.97769 | 1.0038 | -0.0038482 | 4.8735
191 | 1 | 0.97789 | 1.0005 | -0.00050898 | 4.873
192 | 1 | 0.97863 | 0.99729 | 0.0027103 | 4.8757
193 | 1 | 0.97989 | 0.99427 | 0.0057333 | 4.8814
194 | 1 | 0.9816 | 0.99151 | 0.0084917 | 4.8899
195 | 1 | 0.9837 | 0.98907 | 0.010926 | 4.9009
196 | 1 | 0.98613 | 0.98701 | 0.012989 | 4.9139
197 | 1 | 0.98882 | 0.98536 | 0.014643 | 4.9285
198 | 1 | 0.99168 | 0.98414 | 0.015862 | 4.9444
199 | 1 | 0.99463 | 0.98337 | 0.016632 | 4.961
200 | 1 | 0.99761 | 0.98305 | 0.016954 | 4.9779
201 | 1 | 1.0005 | 0.98316 | 0.016835 | 4.9948
202 | 1 | 1.0033 | 0.9837 | 0.016297 | 5.0111
203 | 1 | 1.0059 | 0.98463 | 0.01537 | 5.0264
204 | 1 | 1.0082 | 0.98591 | 0.014093 | 5.0405
205 | 1 | 1.0103 | 0.98749 | 0.012511 | 5.0531
206 | 1 | 1.012 | 0.98932 | 0.010677 | 5.0637
207 | 1 | 1.0133 | 0.99135 | 0.0086474 | 5.0724
208 | 1 | 1.0143 | 0.99352 | 0.0064804 | 5.0789
209 | 1 | 1.0148 | 0.99576 | 0.0042363 | 5.0831
210 | 1 | 1.0149 | 0.99803 | 0.0019748 | 5.0851
211 | 1 | 1.0147 | 1.0002 | -0.00024658 | 5.0848
212 | 1 | 1.0141 | 1.0024 | -0.0023734 | 5.0824
213 | 1 | 1.0132 | 1.0044 | -0.0043559 | 5.0781
214 | 1 | 1.012 | 1.0061 | -0.0061498 | 5.0719
215 | 1 | 1.0105 | 1.0077 | -0.0077175 | 5.0642
216 | 1 | 1.0088 | 1.009 | -0.0090284 | 5.0552
217 | 1 | 1.007 | 1.0101 | -0.01006 | 5.0451
218 | 1 | 1.0051 | 1.0108 | -0.010797 | 5.0343
219 | 1 | 1.0031 | 1.0112 | -0.011232 | 5.0231
220 | 1 | 1.0011 | 1.0114 | -0.011368 | 5.0117
221 | 1 | 0.99914 | 1.0112 | -0.011211 | 5.0005
222 | 1 | 0.9973 | 1.0108 | -0.010779 | 4.9897
223 | 1 | 0.99561 | 1.0101 | -0.010092 | 4.9797
224 | 1 | 0.99409 | 1.0092 | -0.0091784 | 4.9705
225 | 1 | 0.99278 | 1.0081 | -0.0080697 | 4.9624
226 | 1 | 0.99171 | 1.0068 | -0.0068019 | 4.9556
227 | 1 | 0.99089 | 1.0054 | -0.0054132 | 4.9502
228 | 1 | 0.99033 | 1.0039 | -0.0039433 | 4.9463
229 | 1 | 0.99003 | 1.0024 | -0.0024325 | 4.9438
230 | 1 | 0.99 | 1.0009 | -0.00092058 | 4.9429
231 | 1 | 0.99022 | 0.99945 | 0.00055445 | 4.9435
232 | 1 | 0.99068 | 0.99804 | 0.0019569 | 4.9454
233 | 1 | 0.99136 | 0.99675 | 0.0032542 | 4.9487
234 | 1 | 0.99222 | 0.99558 | 0.004418 | 4.9531
235 | 1 | 0.99325 | 0.99458 | 0.0054242 | 4.9585
236 | 1 | 0.99441 | 0.99375 | 0.0062538 | 4.9648
237 | 1 | 0.99566 | 0.99311 | 0.0068929 | 4.9717
238 | 1 | 0.99697 | 0.99267 | 0.0073329 | 4.979
239 | 1 | 0.99831 | 0.99243 | 0.0075707 | 4.9866
240 | 1 | 0.99963 | 0.99239 | 0.0076083 | 4.9942
241 | 1 | 1.0009 | 0.99255 | 0.0074528 | 5.0016
242 | 1 | 1.0021 | 0.99288 | 0.0071157 | 5.0087
243 | 1 | 1.0032 | 0.99339 | 0.0066128 | 5.0153
244 | 1 | 1.0042 | 0.99404 | 0.0059634 | 5.0213
245 | 1 | 1.005 | 0.99481 | 0.0051895 | 5.0265
246 | 1 | 1.0057 | 0.99568 | 0.0043157 | 5.0308
247 | 1 | 1.0062 | 0.99663 | 0.0033679 | 5.0342
248 | 1 | 1.0066 | 0.99763 | 0.0023729 | 5.0366
249 | 1 | 1.0067 | 0.99864 | 0.0013578 | 5.0379
250 | 1 | 1.0067 | 0.99965 | 0.0003488 | 5.0383
251 | 1 | 1.0065 | 1.0006 | -0.00062885 | 5.0376
252 | 1 | 1.0061 | 1.0016 | -0.0015518 | 5.0361
253 | 1 | 1.0056 | 1.0024 | -0.0023989 | 5.0337
254 | 1 | 1.005 | 1.0032 | -0.003152 | 5.0305
255 | 1 | 1.0043 | 1.0038 | -0.0037956 | 5.0267
256 | 1 | 1.0035 | 1.0043 | -0.0043181 | 5.0224
257 | 1 | 1.0027 | 1.0047 | -0.0047111 | 5.0177
258 | 1 | 1.0018 | 1.005 | -0.0049697 | 5.0127
259 | 1 | 1.0009 | 1.0051 | -0.0050929 | 5.0076
260 | 1 | 1 | 1.0051 | -0.0050828 | 5.0026
261 | 1 | 0.99917 | 1.0049 | -0.0049452 | 4.9976
262 | 1 | 0.99837 | 1.0047 | -0.0046884 | 4.9929
263 | 1 | 0.99765 | 1.0043 | -0.0043238 | 4.9886
264 | 1 | 0.99702 | 1.0039 | -0.0038647 | 4.9847
265 | 1 | 0.99649 | 1.0033 | -0.0033265 | 4.9814
266 | 1 | 0.99606 | 1.0027 | -0.002726 | 4.9787
267 | 1 | 0.99576 | 1.0021 | -0.0020806 | 4.9766
268 | 1 | 0.99557 | 1.0014 | -0.0014086 | 4.9752
269 | 1 | 0.9955 | 1.0007 | -0.0007277 | 4.9745
270 | 1 | 0.99555 | 1.0001 | -5.5598e-05 | 4.9744
271 | 1 | 0.99571 | 0.99941 | 0.00059118 | 4.975
272 | 1 | 0.99597 | 0.9988 | 0.0011974 | 4.9762
273 | 1 | 0.99632 | 0.99825 | 0.0017493 | 4.9779
274 | 1 | 0.99675 | 0.99776 | 0.0022352 | 4.9802
275 | 1 | 0.99724 | 0.99735 | 0.0026454 | 4.9828
276 | 1 | 0.99779 | 0.99703 | 0.0029727 | 4.9858
277 | 1 | 0.99836 | 0.99679 | 0.0032122 | 4.989
278 | 1 | 0.99896 | 0.99664 | 0.0033611 | 4.9924
279 | 1 | 0.99956 | 0.99658 | 0.0034195 | 4.9958
280 | 1 | 1.0001 | 0.99661 | 0.0033895 | 4.9992
281 | 1 | 1.0007 | 0.99672 | 0.0032752 | 5.0025
282 | 1 | 1.0012 | 0.99692 | 0.003083 | 5.0055
283 | 1 | 1.0017 | 0.99718 | 0.0028208 | 5.0084
284 | 1 | 1.0021 | 0.9975 | 0.0024979 | 5.0109
285 | 1 | 1.0024 | 0.99788 | 0.002125 | 5.013
286 | 1 | 1.0027 | 0.99829 | 0.0017133 | 5.0147
287 | 1 | 1.0029 | 0.99873 | 0.0012749 | 5.016
288 | 1 | 1.003 | 0.99918 | 0.0008218 | 5.0168
289 | 1 | 1.003 | 0.99963 | 0.000366 | 5.0172
290 | 1 | 1.003 | 1.0001 | -8.0887e-05 | 5.0171
291 | 1 | 1.0028 | 1.0005 | -0.00050797 | 5.0166
292 | 1 | 1.0026 | 1.0009 | -0.00090527 | 5.0157
293 | 1 | 1.0024 | 1.0013 | -0.001264 | 5.0144
294 | 1 | 1.0021 | 1.0016 | -0.0015766 | 5.0128
295 | 1 | 1.0018 | 1.0018 | -0.001837 | 5.011
296 | 1 | 1.0014 | 1.002 | -0.0020409 | 5.009
297 | 1 | 1.001 | 1.0022 | -0.0021852 | 5.0068
298 | 1 | 1.0006 | 1.0023 | -0.0022687 | 5.0045
299 | 1 | 1.0002 | 1.0023 | -0.0022917 | 5.0022
300 | 1 | 0.9998 | 1.0023 | -0.0022562 | 4.9999